# HEBER CAMPUS

## PHASE 2 OPERATING AND FINANCIAL DOCTRINE

Document ID: HC-PH2-001

Revision: A (Draft)

Date: 2025-12-30

Applies To: Phase 2 Expansion (DC + Solar Led Growth)

Related Documents: HC-MGD-001, HC-SFR-001, Appendix H (HRWL)

## 1. PURPOSE

This document formalizes the Phase 2 operating, load management, and financial doctrine for the Heber Campus.

Phase 2 is intended to:

- Maximize return on invested capital (ROI)

- Preserve green compliance

- Avoid premature expansion of firm generation assets

- Leverage data center and solar growth as primary economic drivers

- Maintain fuel production stability

This document is governance-binding for Phase 2 planning, contracting, and dispatch policy.

## 2. PHASE 2 SCOPE DEFINITION

### 2.1 Included Assets

Phase 2 includes the following incremental expansions beyond Phase 1:

- Data Centers: Expansion up to 8 buildings total

  - 50 MW IT load per building

  - 400 MW IT total

- Solar Generation: Expansion from 1.5 GW to approximately 3.0 GW

- Cooling Infrastructure:

  - Modular central NH3 cooling plant (N+1)

  - Closed-loop geothermal borefield expansion

  - Free cooling prioritized at all times

- Hydrogen and Fuels:

  - SOEC capacity unchanged at 457 t/day H2

  - Finished fuels unchanged at 18,000 bpd

- Firm Generation:

  - 12 NuScale VOYGR SMR modules

  - 100 MW biomass plant

No additional SMRs or fuel expansion is assumed in Phase 2.

## 3. PHASE 2 OPERATING PRINCIPLE

Phase 2 operates under a managed scarcity doctrine during nighttime hours.

Nighttime load is treated as a constrained resource window. MECSAI is authorized to actively shape demand across controllable loads to maintain green compliance without reliance on backup fuels.

Daytime operation prioritizes:

- Fuel production catch-up

- Data center batch processing

- Power export

## 4. LOAD MANAGEMENT DOCTRINE

### 4.1 Firm Night Supply

- Net firm night capacity: approximately 922 MW

  - 12 SMRs + biomass after station service

This value is treated as a hard ceiling for nighttime internal consumption.

### 4.2 Night Load Categories

Nighttime loads are classified as follows:

- Must-Run Loads

  - Safety systems

  - Core DC Tier 0 and Tier 1 services

  - Minimum SOEC hot-standby band

  - Critical chemical plant operations

- Shiftable Loads

  - DC Tier 2 batch workloads

  - SOEC production above minimum band

  - Chemical compression and transfer tasks

- Curtailable Loads

  - Non-critical DC compute

  - Auxiliary processing

### 4.3 Night Load Control Targets (Phase 2)

| Load Category | Target Night Action |
| --- | --- |
| Data Centers | Up to 35–40% IT deferrable at night |
| SOEC | Reduce to 70–75% of average (current density only) |
| Chemical Plant | Shift 10–20 MW of compression/transfer to day |

These controls are enforced automatically by MECSAI and contractually enabled.

## 5. DATA CENTER OPERATING DOCTRINE

### 5.1 Contract Structure

All Phase 2 DC contracts shall:

- Define Tiered workload classes (Tier 0, 1, 2)

- Permit nighttime throttling of Tier 2 workloads

- Allow daytime overdrive for deferred processing

### 5.2 Cooling Doctrine

- Cooling priority order:

  - Free cooling

  - Geothermal heat rejection

  - NH3 compressors (last resort)

- Nighttime PUE target: <= 1.18

- Daytime PUE target: ~1.28

## 6. SOEC OPERATING DOCTRINE

- SOEC remains in continuous hot-standby operation

- No thermal cycling is permitted

- Night reduction is achieved via current density modulation only

- Daytime overproduction (up to 135–150%) is permitted

- Hydrogen storage is used to maintain steady fuel synthesis cadence

## 7. POWER EXPORT DOCTRINE

### 7.1 Firm Export Commitments

- Phase 2 firm export limit: 50 MW 24/7

- Backed exclusively by SMR + biomass

- No solar dependence

### 7.2 Flexible Export

- Daytime flexible export prioritized

- Night exports are opportunistic only

- No export commitment shall force SOEC reduction or fuel burn

## 8. FINANCIAL BASELINE (PHASE 2)

### 8.1 Annual Revenue (Conservative)

| Source | Annual Revenue |
| --- | --- |
| Data Centers | ~$720M |
| Fuels | ~$566M |
| Power Exports | ~$150M |
| Total | ~$1.4B |

### 8.2 Annual Operating Costs

| Category | Annual Cost |
| --- | --- |
| Fuel Production | ~$365M |
| Nuclear O&M | ~$100M |
| Biomass O&M + Feedstock | ~$50M |
| DC OPEX | ~$72M |
| Labor & Admin | ~$121M |
| Misc / Insurance | ~$55M |
| Total OPEX | ~$763M |

### 8.3 EBITDA and Cash Flow

- EBITDA: approximately $640M/year

- Estimated debt service: ~$370M/year

- Net cash flow: ~$270M/year

## 9. EXPANSION TRIGGERS (PHASE 3)

Phase 3 expansion (additional SMRs, SOECs, fuels) shall not commence until all of the following are met for at least 12 consecutive months:

- DC utilization >= 90%

- SOEC uptime >= 95%

- Fuel production >= 95% of nameplate

- DSCR >= 1.40x

- Night load management achieved without backup fuel use

## 10. GOVERNANCE

- This document is binding for Phase 2 operations

- Deviations require governance approval

- MECSAI enforcement logs shall be retained

- Revisions must be versioned and archived

END OF DOCUMENT