# APPENDIX H

## Heat Recovery Water Loop (HRWL) Architecture and Control Doctrine

Document ID: HC-SFR-001-APP-H

Revision: A

Status: Draft – Governance Review

Related Documents: HC-SFR-001, HC-MGD-001

## H.1 PURPOSE AND SCOPE

This appendix defines the Heat Recovery Water Loop (HRWL) architecture and operating doctrine for the Heber Campus.

The HRWL is a secondary thermal recovery system designed to capture low- and medium-grade waste heat from campus cooling systems (primarily the central ammonia refrigeration plant and data center cooling loops) and redistribute that heat to approved process water applications.

This appendix establishes:

- Physical system boundaries

- Approved heat recovery interfaces

- Heat Sink Registry requirements

- Control hierarchy and MECSAI authority limits

- Safety and contamination constraints

- Modularity and expansion rules

This appendix does not override HC-MGD-001; it supplements it with a formal thermal-integration control layer.

## H.2 SYSTEM ARCHITECTURE OVERVIEW

### H.2.1 HRWL Definition

The HRWL is a closed, isolated water-based loop (water or water/glycol as required for freeze protection) that:

- Receives heat via heat exchangers only from:

  - Central NH₃ refrigeration plant condenser circuits

  - Data center secondary cooling loops

- Distributes heat to registered process water sinks

- Rejects excess heat when no sinks are available

Direct fluid contact between NH₃ and any water system is prohibited.

### H.2.2 Thermal Priority Stack (Cooling First)

The HRWL operates under the following immutable priority order:

- Data center cooling reliability

- NH₃ plant safety and stability

- Heat recovery to HRWL sinks

- Heat rejection (free cooling → geothermal → compressors)

Heat recovery shall never compromise cooling reliability.

## H.3 PHYSICAL SYSTEM BOUNDARIES

### H.3.1 Allowed Interfaces

| Interface | Allowed | Notes |
| --- | --- | --- |
| NH₃ → HRWL | YES | Via HX only |
| HRWL → Process Water | YES | Via HX only |
| NH₃ → Process Water | NO | Prohibited |
| HRWL → Borefield | OPTIONAL | Via HX only |
| HRWL → Cooling Loops | NO | One-way thermal extraction only |

### H.3.2 Required Components

Each HRWL installation shall include:

- Plate or shell-and-tube heat exchangers (HX-rated for duty)

- HRWL circulation pumps with VFDs

- Thermal buffer tank (see H.4)

- Isolation valves and bypass lines

- Flow meters (supply and return)

- Temperature sensors (inlet/outlet per branch)

- Pressure relief and expansion control

- Freeze protection (where required)

## H.4 THERMAL BUFFER TANK REQUIREMENTS

### H.4.1 Purpose

The HRWL thermal buffer tank provides:

- Decoupling between fluctuating heat sources and steady process sinks

- Ramp-rate smoothing

- Thermal storage for short-term mismatches

- Protection against water hammer and thermal shock

### H.4.2 Design Requirements

- Sized to absorb minimum 15–30 minutes of peak recoverable heat

- Minimum and maximum temperature limits enforced

- Level monitoring with high/low interlocks

- Bypass to heat rejection when tank is saturated

- Freeze protection logic enabled

## H.5 HEAT SINK REGISTRY (MANDATORY)

### H.5.1 Registry Concept

“Process water” is defined as any pre-approved thermal sink registered in the Heat Sink Registry.

MECSAI may not route heat to any destination not explicitly registered.

### H.5.2 Required Registry Fields

Each Heat Sink entry shall include:

- Sink_ID (unique identifier)

- Sink_Type (e.g., feedwater preheat, RO feed, building heat)

- Allowed temperature range (in/out)

- Maximum heat acceptance (MWth)

- Maximum delta-T

- Availability schedule (continuous / batch / seasonal)

- Priority class:

  - Critical

  - Preferred

  - Opportunistic

- Water quality constraints

- Isolation and control valve IDs

- Safety interlocks

- Economic value coefficient (optional)

### H.5.3 Typical Registered Sink Examples

- Boiler feedwater preheat

- RO/DI feedwater preheat

- Chemical plant process water

- Space heating loops

- Freeze protection loops

## H.6 CONTROL DOCTRINE (MECSAI AUTHORITY)

### H.6.1 MECSAI Authority

MECSAI is authorized to:

- Allocate recovered heat among registered sinks

- Modulate HRWL flows and valve positions

- Manage buffer tank charge/discharge

- Reject heat when sinks are unavailable

MECSAI is not authorized to:

- Create new heat sinks

- Bypass safety interlocks

- Modify plumbing topology

- Compromise cooling reliability

### H.6.2 Control Hierarchy

At each control interval, MECSAI shall:

- Verify DC cooling and NH₃ plant constraints are satisfied

- Determine available recoverable heat (MWth)

- Query Heat Sink Registry for active sinks

- Allocate heat by:

  - Priority class

  - Economic value

  - Operational constraints

- Enforce ramp limits on valves and pumps

- Reject excess heat if no sinks are available

## H.7 SAFETY AND COMPLIANCE REQUIREMENTS

- NH₃ detection and emergency response systems are independent of HRWL

- No single HX failure shall permit cross-contamination

- Double-wall HX or HX-in-series required for sensitive sinks

- All HRWL branches require:

  - Isolation valves

  - Check valves where applicable

  - Temperature and flow monitoring

- HRWL shall fail safe to heat rejection, not to process sinks

## H.8 MODULARITY AND EXPANSION RULES

- Each new DC building shall add:

  - One HRWL HX interface

  - Additional buffer or pumping capacity as required

- Each new NH₃ cooling block shall include:

  - Dedicated HRWL recovery HX

- Each new heat sink must be:

  - Engineered

  - Approved

  - Registered

  - Tested

before MECSAI activation

Expansion shall follow the campus modular replication doctrine defined in HC-SFR-001.

## H.9 GOVERNANCE

- HRWL design changes require governance approval

- Heat Sink Registry modifications require documented review

- This appendix supports, but does not override, HC-MGD-001

- Superseded revisions must be archived

END OF APPENDIX H