MINIMAL OPTION SHEET

(Mandatory for Bid Qualification)

Purpose: Ensure safe, warranty-compliant observability for MECSAI integration without modifying the SOEC stack.

### 1. Sensor Scope (OEM supplied or OEM approved)

Vendor shall provide or approve the following sensors at OEM-defined interfaces:

- Stack inlet temperature (H2 and O2 sides)

- Stack outlet temperature (H2 and O2 sides)

- Stack average temperature

- Stack inlet pressure (H2 and O2 sides)

- Stack outlet pressure (H2 and O2 sides)

- DC bus voltage

- DC bus current

- Hydrogen purity or crossover indication (binary acceptable)

All sensors must be:

- OEM installed OR OEM approved

- OEM calibrated

- Covered under standard warranty

### 2. Data Access Requirements

Vendor shall provide read-only access to the following data streams:

- Raw sensor values (not alarm-only)

- Minimum sampling rate: 1 Hz

- Protocols supported:

  - Modbus TCP

  - OPC-UA

  - EtherNet/IP (acceptable)

No write access to safety systems is required.

### 3. Control Authority

- Vendor PLC retains full safety and interlock authority

- External systems (MECSAI) may issue:

  - Start/stop requests

  - Power setpoints

  - Ramp rate limits

- Vendor PLC may override external commands at any time

### 4. Warranty Protection

Contract language shall explicitly state:

- External monitoring does not void warranty

- External analytics and logging are permitted

- External derating commands upstream of OEM PLC are allowed

DESIRED OPTION SHEET

(Preferred Partnership Configuration)

Purpose: Enable predictive health monitoring, lifetime optimization, and MECSAI-certified plant operation.

### 1. Enhanced Sensor Package (OEM installed)

Vendor to integrate the following additional sensors:

Thermal:

- Multiple thermocouples per stack face (minimum 4)

- Thermal gradient monitoring across stack depth

- Stack ramp-rate calculation support

Electrical:

- Stack-level voltage sense taps

- High-resolution current transducer

- Optional cell-group voltage taps (vendor discretion)

Gas Quality:

- Hydrogen moisture sensor (ppm resolution)

- Oxygen side humidity sensor

- Differential pressure decay measurement ports

Mechanical (non-intrusive):

- External vibration sensors

- External acoustic emission sensor (optional)

All sensors remain within OEM mechanical and thermal design limits.

### 2. High-Resolution Data Access

Vendor to provide:

- Raw sensor data access

- Minimum sampling rate:

  - Electrical: 10 Hz

  - Thermal: 2 Hz

- Timestamped data with synchronized clock

- Health and diagnostic flags exposed as variables (not just alarms)

### 3. MECSAI Interface Support

Vendor agrees to:

- Publish interface control document (ICD)

- Define allowable external command envelope

- Support MECSAI as a read-only supervisory system

- Participate in joint validation testing (FAT / SAT)

### 4. Compliance and Certification Path

Vendor agrees to collaborate on:

- MECSAI-ready certification language

- Reference architecture documentation

- Optional co-marketing:

  - “MECSAI-Compatible SOEC Platform”

  - Joint white papers and case studies

- Operator-facing documentation highlighting:

  - Compliance

  - Predictive maintenance

  - Extended stack life

### 5. Commercial Framework (Non-Binding)

- No exclusivity required

- MECSAI branding permitted in vendor materials

- Vendor branding permitted in MECSAI deployments

- Future integration roadmap optional

BOTTOM LINE POSITIONING FOR VENDORS

This is not a control takeover.

This is observability, longevity, and compliance acceleration.

You are not asking them to:

- Change their stack chemistry

- Hand over IP

- Surrender safety authority

You are offering them:

- A premium monitoring layer

- Reduced warranty risk

- Differentiation in a crowded SOEC market

- A path to MECSAI-driven demand

NEXT STEPS (YOUR CHOICE)

I can:

- Convert this into a formal RFP exhibit

- Add legal-ready warranty clauses

- Create a vendor pitch deck

- Draft a MECSAI certification badge and definition

- Or tailor this to a specific OEM profile (EU vs US vs Asia)

Tell me how aggressive you want to be and who the first targets are.