DC-BLDG-INST-MAP-001

Building 1 Instrumentation & Sensor Map – Rev A
Applies to: Building 1 (POC)
Replication Baseline: Buildings 2–16

1. PURPOSE

1.1 This document defines the mandatory instrumentation layout for Building 1.

1.2 Building 1 is designated as the Proof-of-Concept (POC) facility and shall be instrumented beyond steady-state operational needs to capture:

- performance envelopes

- degradation trends

- fault precursors

- operational correlations

1.3 Instrumentation explicitly does not participate in protection or control.
Hardware protection clears faults. Sensors observe.

2. INSTRUMENTATION PHILOSOPHY (NON-NEGOTIABLE)

2.1 Separation of concerns:

- Sensors observe

- SCADA records

- MECSAI analyzes

- Hardware protects

2.2 No sensor, PLC, SCADA, or AI system may:

- clear electrical faults

- close isolation valves

- reset breakers

- override interlocks

2.3 All instrumentation must:

- fail safe

- default to “unknown” rather than “normal”

- not impair operations if offline

3. INSTRUMENTATION ZONES

Instrumentation is defined across six physical domains:

- Rack-level (sampled)

- Pod group

- CDU group

- Zone (150-ft segment)

- Utility bay

- Building-level

4. RACK-LEVEL INSTRUMENTATION (POC-ONLY, SAMPLED)

Rack-level instrumentation is sampled, not universal.

4.1 Coverage

- 1 rack per pod group (32 racks)

- 32 racks instrumented total (POC sample set)

4.2 Sensors

- Rack input power (kW, current, voltage)

- Cold plate inlet temp

- Cold plate outlet temp

- Rack inlet air temp (residual)

- Rack exhaust air temp

- Vibration (low-frequency)

- Acoustic baseline (broadband)

4.3 Purpose

- validate vendor claims

- correlate power ramps to thermal response

- detect early mechanical degradation

- tune envelope limits

4.4 Replication rule

- Rack-level instrumentation is not required in Buildings 2–16 unless justified by POC findings.

5. POD GROUP INSTRUMENTATION (MANDATORY, REPLICATED)

Each 32-rack pod group shall include:

5.1 Electrical

- Pod group power meter

- Voltage deviation logger

- Transient capture (event-based)

5.2 Cooling

- Coolant supply temperature

- Coolant return temperature

- Coolant flow rate

- Delta-P across pod group

- Leak detection at interface panel

5.3 Status

- Pod isolation valve position

- Pod availability state

5.4 Purpose

- enforce envelope limits

- detect degradation

- localize faults rapidly

This instrumentation replicates to all buildings.

6. CDU GROUP INSTRUMENTATION (MANDATORY)

Each CDU pair shall include:

6.1 Hydraulic

- Supply temperature

- Return temperature

- Flow rate per CDU

- Pump speed

- Pump power draw

- Filter differential pressure

6.2 Safety

- Underpan leak detection

- CDU internal alarm states

6.3 Thermal margin

- Available thermal headroom (calculated)

- Saturation warning thresholds

6.4 Purpose

- predict pump wear

- detect fouling

- identify thermal bottlenecks before failure

7. ZONE-LEVEL INSTRUMENTATION (150-FT ZONES)

Each zone (A–D) shall include:

7.1 Electrical

- Zone aggregate power meter

- Ramp rate monitoring

- Zone fault counters

7.2 Cooling

- Zone supply/return headers temp

- Zone aggregate flow

- Zone delta-T

7.3 Environmental

- Ambient temp (compute bay)

- Ambient temp (utility bay)

- Relative humidity (utility bay only)

7.4 Purpose

- zone-level isolation decisions

- validate ramp envelopes

- correlate thermal behavior with workload patterns

8. UTILITY BAY INSTRUMENTATION

8.1 Drainage

- Trench drain flow presence sensors

- High-water detection at drain low points

8.2 Leak monitoring

- Distributed leak detection cable along:

  - CDU rows

  - interface panels

  - trench drain perimeter

8.3 Mobility and operations

- Scooter docking status

- Robot docking status

- Battery charge state (fleet-level)

Purpose:

- detect spills early

- correlate maintenance activity with events

- support operational analytics

9. BUILDING-LEVEL INSTRUMENTATION

9.1 Electrical

- Building DC intake meters

- Building transient and harmonic monitors

- Ground reference monitoring

9.2 Thermal

- Building secondary loop supply/return

- HRWL interface temps (if active)

- Total rejected heat (MW)

9.3 Structural (POC-only)

- Roof deflection monitors (sample points)

- Truss vibration sensors (sampled)

Purpose:

- validate structural assumptions

- correlate snow load and internal load behavior

Structural sensors may be removed or reduced after POC.

10. DATA HANDLING AND RETENTION

10.1 Data ownership:

- Owner retains full ownership of all raw data

- No down-sampling without approval

10.2 Retention:

- High-rate data: minimum 30 days

- Event-triggered captures: permanent retention

- Aggregated metrics: lifetime

10.3 Time sync:

- All sensors must be time-synchronized (PTP or equivalent)

11. MECSAI INTEGRATION RULES

11.1 MECSAI access:

- Read-only access to all instrumentation

- No write authority to control devices

11.2 MECSAI functions:

- trend analysis

- anomaly detection

- correlation analysis

- predictive maintenance recommendations

11.3 MECSAI must never:

- command valves

- command breakers

- bypass hardware protections

12. PROOF-OF-CONCEPT EXIT CRITERIA

Building 1 instrumentation shall remain active until:

- 12 months of stable operation

- envelope limits validated

- degradation trends characterized

- no systemic anomalies unresolved

Post-POC:

- Non-essential sensors may be reduced

- Replication profile finalized for Buildings 2–16

13. REPLICATION PROFILE SUMMARY

| Instrumentation Type | Building 1 | Buildings 2–16 |
| --- | --- | --- |
| Rack-level sensors | Sampled | No |
| Pod group sensors | Yes | Yes |
| CDU sensors | Yes | Yes |
| Zone sensors | Yes | Yes |
| Structural sensors | Yes | No |
| Mobility analytics | Yes | Optional |