DC-BLDG-PLAN-NOTES-001

Data Center Interior Architecture – Rev A Plan Notes
Applies to: Buildings 1–16 (Building 1 = Instrumented POC)

1. GENERAL INTENT

1.1 These plan notes define mandatory architectural, structural, mechanical, electrical, and operational constraints for the Heber Campus AI Data Center Buildings.

1.2 Building geometry, rack layout, pod structure, and service zoning are intentionally fixed to support:

- modular replication

- deterministic operations

- fault isolation

- long-term OPEX minimization

1.3 Deviations from these notes require written owner approval. Value engineering that compromises operations is prohibited.

2. BUILDING GEOMETRY (LOCKED)

2.1 Building footprint:

- 160 ft (W) x 600 ft (L) = 96,000 sqft

- Single-story construction

2.2 Interior clear height:

- Minimum 30 ft clear from finished floor to lowest obstruction

2.3 Structural grid:

- Roof trusses at 10 ft on center

- Single structural column line permitted only at the 60 ft / 100 ft bay interface

- No columns permitted within the compute bay footprint

3. BAY DEFINITIONS

3.1 Compute Bay

- Width: 100 ft clear span

- Purpose: IT racks and aisles only

- Prohibited:

  - CDUs

  - valve stations

  - wet maintenance

  - parts storage

  - scooters or robots

3.2 Utility Bay

- Width: 60 ft

- Finished floor elevation: 12 inches lower than compute bay

- Floor slope: 1–2 percent toward central trench drain

- Purpose:

  - cooling distribution

  - electrical distribution

  - fiber distribution

  - service nodes

  - wet maintenance

  - technician mobility

  - robotic logistics

4. COMPUTE BAY RACK LAYOUT

4.1 Rack blocks across width:

- Four (4) double-row blocks

- Each block width: 24 ft

- Total rack block width: 96 ft

- Remaining width: 2 ft buffer at each exterior wall

4.2 Double-row block geometry:

- Cold aisle: 5 ft

- Rack depth zone: 5 ft

- Hot aisle: 4 ft

- Rack depth zone: 5 ft

- Cold aisle: 5 ft

4.3 Rack rows:

- Eight (8) total rack rows across compute bay width

5. LENGTH SEGMENTATION AND ZONING

5.1 Building length segmentation:

- Zone A: 0–150 ft

- Zone B: 150–300 ft

- Zone C: 300–450 ft

- Zone D: 450–600 ft

5.2 Cross aisles:

- Zone boundary cross aisles: minimum 10 ft

- Mid-zone cross aisles: minimum 10 ft

5.3 Purpose of zoning:

- limit incident scope

- define power and cooling fault domains

- reduce technician travel distance

- align service nodes with operational zones

6. POD STANDARD (LOCKED)

6.1 Pod definition:

- Pod size: 32 racks

- Pod is the atomic unit for:

  - power distribution

  - cooling distribution

  - leak detection

  - operational ownership

  - tenant allocation

6.2 Pod density:

- Eight (8) pods per 150 ft zone

- 256 racks per zone

- 1,024 racks per building (Rev A baseline)

7. COOLING ARCHITECTURE RULES

7.1 Cooling method:

- Direct-to-chip liquid cooling assumed

- Ammonia refrigerant prohibited inside building

7.2 CDU placement:

- CDUs shall be located only in the utility bay

- One (1) N+1 CDU pair per pod group

7.3 Leak containment:

- All CDU groups shall include:

  - leak sensor underpan

  - gravity drain to utility bay trench

  - isolation valves at supply and return

- Wet work prohibited in compute bay

8. POWER DISTRIBUTION RULES

8.1 Power delivery:

- Power enters building via wall penetrations only

- Overhead busway distribution within building

8.2 Protective domains:

- Power fault domains align with:

  - pod groups

  - zone boundaries

- Hardware protection devices clear faults autonomously

8.3 Control systems:

- MECSAI may monitor and analyze

- MECSAI may not clear faults or operate breakers

9. UTILITY BAY LAYOUT AND OPERATIONS

9.1 Floor drainage:

- Continuous central trench drain full building length

- Cleanouts required at each service node

9.2 Mobility lanes:

- Scooter lane: minimum 6 ft clear

- Robot lane: minimum 4 ft clear

- Scooters and robots prohibited in compute bay

9.3 Service nodes:

- One service node per zone boundary (minimum)

- Service nodes include:

  - parts storage

  - workstations

  - cable make-up/testing

  - scooter charging

  - robot charging

  - spill kits and wet maintenance bench

10. ROOF AND ENVELOPE RULES (SUMMARY)

10.1 Roof:

- Dual slope standing seam metal roof

- Roof overhang beyond tilt-up walls

- Zero roof penetrations permitted

10.2 Drainage:

- External concealed gutters outside building envelope

- Downspouts external to tilt-up walls

- Downspouts connect to underground storm system away from foundations

10.3 Foundations:

- Tilt-up panels seated in recessed slab edge (minimum 6 inch lip)

- Finished grade and sidewalks slope away from building perimeter

11. BUILDING 1 – PROOF OF CONCEPT ADDITIONS

11.1 Instrumentation density:

- Additional sensors permitted in Building 1:

  - power quality

  - thermal gradients

  - leak detection

  - vibration and acoustics

- Extra conduit and pull strings encouraged

11.2 Overbuild allowance:

- Building 1 may include:

  - oversized CDU capacity

  - additional spare service node capacity

  - expanded test racks

- No reduction of geometry or standards allowed

11.3 Replication rule:

- Lessons learned from Building 1 may inform refinements

- Geometry and zoning for Buildings 2–16 remain unchanged unless formally revised

12. PROHIBITIONS (NON-NEGOTIABLE)

- No roof penetrations

- No internal floor drains in compute bay

- No wet maintenance in compute bay

- No scooters or robots in compute bay

- No reduction of aisle widths

- No vendor-driven geometry changes