HDS Rack Slot Interface Control Document (ICD)
Slot S/H/X - Power, Liquid, Fiber, Telemetry Interfaces

Document ID: HDS-DC-SLOT-ICD-001
Revision: Rev A
Status: Draft - Internal
Owner: Atlas Systems Group - Hermes Data Systems
Date: 2026-01-12

# 1. Purpose

Define a vendor-agnostic rack slot interface standard for Hermes data centers. This ICD ensures any rack or accelerator ecosystem can be deployed and refreshed without reengineering building infrastructure.

# 2. Scope

Applies to all rack deployments in Hermes buildings (terrestrial and future orbital translations). Defines the physical and logical interfaces at the Pod Group Interface Panel and rack manifold entry.

# 3. Definitions

- Rack Slot: A standardized envelope for rack power, cooling, physical footprint, and interface connectors.
- Slot S: Standard rack class (80-120 kW sustained).
- Slot H: High density rack class (120-180 kW sustained).
- Slot X: Experimental rack class (180-250 kW sustained; limited pods only).
- Pod Group: 32-rack pod allocation unit.
- Interface Panel: The standardized wall/partition interface between utility bay distribution and compute bay pod group drops.

# 4. Slot Envelope Summary

Slot S:
- Sustained rack power: 80-120 kW
- Burst (<=5 min): up to 140 kW

Slot H:
- Sustained rack power: 120-180 kW
- Burst (<=5 min): up to 210 kW

Slot X:
- Sustained rack power: 180-250 kW
- Burst (<=5 min): up to 300 kW
- Deployment limited to designated Slot X pods only

# 5. Power Interface Standard

5.1 Building Distribution Assumptions

- Building distribution: overhead DC busway trunks with pod group tap boxes in utility bay.
- Rack feeds: distributed from pod group tap boxes to racks via overhead drops.
- Protection: hardware-cleared fault domains; no software-dependent clearing.

5.2 Electrical Interface at Pod Group Panel

- Feed type: DC (nominal 800 VDC architecture at building/campus level).
- Rack-level conversion: allowed inside rack (vendor-defined) provided it does not violate envelope.
- Tap box outputs: standardized DC feeders per pod group.
- Connector standard: vendor-neutral, field-serviceable, lockable disconnect at interface panel.
- Cable routing: overhead drops; no underfloor power distribution in compute bay.

5.3 Electrical Ratings (Design Targets)

- Voltage window at pod group panel: 700-900 VDC (planning band; final by electrical engineer and procurement).
- Rack feeds: multiple parallel feeders permitted.
- Grounding/bonding: dedicated equipment grounding conductor and bonding bus per pod group.

5.4 Required Power Telemetry Points

- Rack input kW (sampled or per-rack depending on building instrumentation tier).
- Pod group aggregate kW (mandatory).
- Voltage and current at pod group panel (mandatory).
- Event-based transient capture at pod group panel (Building 1 mandatory; others optional by policy).

# 6. Liquid Cooling Interface Standard

6.1 Thermal Envelope (Mandatory)

- Coolant supply nominal: 30 C
- Preferred band: 28-32 C
- Max sustained: 35 C
- Absolute transient ceiling: 38 C
- Sub-ambient coolant is prohibited (no chilled dependency).
- Ammonia refrigerant is prohibited inside building; heat transfer via HX only.

6.2 Fluid Type

- Primary: water or water/glycol as required for freeze protection.
- Dielectric fluids: prohibited unless explicitly approved for a dedicated lane and supported by containment plan.

6.3 Mechanical Interface at Pod Group Panel

- Two connections minimum per pod group: supply and return.
- Connector type: quick-disconnect, dry-break, keyed to prevent mis-mate.
- Materials: stainless steel or approved corrosion-resistant alloy.
- Isolation: manual isolation valves at CDU group and at interface panel (mandatory).
- Leak detection: sensor at interface panel and under CDU underpan (mandatory).

6.4 Hydraulic Requirements (Declaration by Vendor)

Each rack vendor must declare:
- Required flow rate at 80, 120, 150, 180, 250 kW (as applicable)
- Delta-P across rack manifold at nominal flow
- Acceptable supply temperature band
- Coolant chemistry constraints (inhibitors, glycol percentage, conductivity limits)
Racks exceeding Hermes delta-P planning envelope require explicit approval.

# 7. Fiber and Network Interface Standard

7.1 Physical Interface

- Fiber trunks originate in utility bay and enter pod groups through the interface panel.
- Connector standard: LC/UPC or MPO/MTP as required by lane, terminated in patch panels.
- Cable management: overhead trays; service loops maintained in utility bay.

7.2 Lane Strategy Note

Accelerator ecosystems may require different fabrics. Hermes supports lane segregation at the pod level. Mixed lanes within a pod are prohibited.

# 8. Telemetry and Tagging Standard

8.1 Required Telemetry (Minimum Set)

- Pod group power: kW, volts, amps, event flags
- CDU group: supply/return temps, flow, pump speed, pump power, filter delta-P
- Pod group cooling: supply/return temps, flow, delta-P
- Leak sensors: status, time of first detection
- Valve positions: isolation valves (open/closed)
- Environmental: utility bay temp/humidity, compute bay ambient temp

8.2 Topic and Tag Naming (Baseline)

Tag format:
HDS.<SITE>.<BLDG>.<ZONE>.<PODGROUP>.<SUBSYSTEM>.<POINT>

Examples:
HDS.HEBER.B01.ZA.PG01.PWR.KW
HDS.HEBER.B01.ZB.PG03.CDU1.SUPPLY_TEMP
HDS.HEBER.B01.ZC.PG05.LEAK.IFPANEL

# 9. Acceptance Tests at Rack Slot Level

- Verify physical fit and clearances
- Verify power interface compatibility and grounding
- Verify cooling interface compatibility and leak-free connection
- Verify declared flow and delta-P within limits
- Verify telemetry points and time synchronization
- Perform power ramp and thermal ramp tests within envelope
- Confirm no requirement for sub-ambient cooling

# 10. Prohibitions

- Racks requiring chilled coolant (<20 C) are prohibited.
- Ammonia inside building is prohibited.
- Mixed accelerator lanes within a pod are prohibited.
- Interface changes without approval are prohibited.

# 11. Revision Control

Rev A establishes baseline ICD. Connector part numbers and final voltage windows are finalized at procurement time and must remain backward compatible across refresh generations.