Below is a clean, structured reference document summarizing this entire discussion.
It is written so you can drop it into your project folder and use it as a design and decision record going forward.

MECSAI RACK INFRASTRUCTURE DESIGN SUMMARY

Location: Heber-Overgaard, AZ
Use Case: AI compute + NAS infrastructure inside a client-facing office

1. Objectives

- Replace aging NAS (WD EX4100) with modern, fast, rack-mounted infrastructure

- Support local AI execution (MECSAI) with GPU acceleration

- Maintain modular headroom (start small, expand cleanly)

- Keep system air-cooled, serviceable, and reliable

- Integrate infrastructure into a professional office environment

- Use heat output beneficially in winter; manage cooling in summer

2. Core Architecture Decision

Single Rack, Two Nodes

The final architecture uses one rack with separated roles:

- NAS Node (Storage Authority)

  - Enterprise storage

  - ZFS or BTRFS

  - ECC memory

  - Snapshots and replication

  - Authoritative data source

- Compute Node (AI + MECSAI Execution)

  - Dual-socket CPU platform

  - GPU acceleration

  - Large local NVMe scratch tier (~30TB)

  - Containerized AI workloads

  - Expandable GPU count

Nodes are interconnected by a high-capacity switch (10Gb minimum, 25Gb preferred).

This separation avoids performance contention, improves reliability, and allows independent upgrades.

3. Compute Platform Choice

CPU Strategy: B1 – High Core Count

- Dual Intel Xeon Gold 6248R

- Reason: ability to run multiple software stacks concurrently (AI, orchestration, services)

- Prioritizes parallel execution over single-thread performance

- Future-proof and cost-effective via used/refurb market

4. GPU Strategy

Phase-Based Expansion

- Platform supports up to 4 GPUs

- Initial deployment: 1–2 consumer GPUs

- Future expansion: up to 4 GPUs or mixed fleet

Initial GPU Choice

- NVIDIA RTX 4090 (or equivalent)

- High performance per dollar

- Strong CUDA ecosystem

- Adequate for inference and moderate training

Future Upgrade Path

- NVIDIA A5000 / A6000 / L40-class GPUs

- Higher VRAM and ECC support

- Platform does not need to change

This avoids over-spending early while preserving long-term options.

5. Storage Architecture

NAS Node

- Enterprise rack chassis (Supermicro-class)

- ECC RAM

- ZFS (TrueNAS SCALE recommended)

- HDD pool for capacity

- Snapshot + replication capability

Local NVMe Tier (Compute Node)

- ~30TB raw capacity

- 4 × 7.68TB enterprise NVMe drives

- Used for:

  - Model weights

  - Embeddings

  - Datasets

  - High-IO scratch

- Prevents AI workloads from hammering NAS

6. Networking

- Backbone: 25Gb preferred (10Gb minimum acceptable)

- Switch supports:

  - SFP+/SFP28

  - LACP

  - VLANs

- Used/refurb Mellanox NICs acceptable

- Avoid consumer networking hardware

7. Cooling Strategy

Cooling Type: Air-Cooled (Intentional Decision)

Reasons:

- Reliability

- Serviceability

- Lower cost

- No leak risk

- Easier GPU upgrades

Liquid cooling is unnecessary at this scale (≤4 GPUs).

Thermal Load Estimates

- Phase 1 (1–2 GPUs): ~1.5–2.2 kW (~5,100–7,500 BTU/hr)

- Phase 2 (4 GPUs): ~2.5–3.5 kW (~8,500–12,000 BTU/hr)

This aligns closely with existing space heater usage.

8. Building Suitability

Building: 12×28 Graceland structure, fully insulated

Winter

- Current heating: 1–2 × 1500W space heaters

- Compute rack replaces heaters effectively

- Net benefit

Summer

- Existing window AC units (~4k + 8k BTU) adequate for Phase 1

- Phase 2 requires upgrade

Recommended Upgrade

- 18,000 BTU inverter mini-split

- Provides margin for 4-GPU load

- Quiet, efficient, continuous duty

- Improves thermal stability and noise

9. Airflow Design Rules

Key Principle

Do NOT aim AC return directly at the rack intake.

Reason:

- Creates thermal short-circuit

- Eliminates room buffering

- Hides instability until sudden failure

- Causes recirculation and throttling

Correct Approach

- Rack breathes room air

- AC conditions the room

- Exhaust allowed to mix and rise naturally

- Room acts as thermal buffer

10. Rack Placement in Office

Constraints

- Client-facing office

- Professional appearance

- Quiet operation

- No center-room placement

Recommended Placement

- Along a long wall

- Offset 12–24 inches from wall

- Rear exhaust flows upward and outward

- Front intake unobstructed

- Blanking panels in unused rack space

Rack Characteristics

- Short rack (12U–24U)

- Black, enclosed sides

- Perforated front/rear doors

- Clean cable management

Result: intentional, professional appearance without visual dominance.

11. Noise Management

- Stable intake temperatures prevent fan ramping

- Airflow discipline reduces noise spikes

- Heavy AI workloads scheduled outside client meetings

- Mini-split keeps fan curves steady

Proper airflow matters more than soundproofing.

12. Role of Existing Hardware (EX4100, GSA-1000)

WD EX4100

- No longer primary storage

- Optional use as backup sink only

- RAID can be broken for mirror/archive role

GSA-1000

- Remains valid workstation

- Acts as:

  - Operator console

  - Development node

  - Secondary compute (optional)

- Requires network upgrade (10/25Gb NIC)

- Does not need to move into rack

13. Summary Conclusions

- Architecture is sound, scalable, and office-appropriate

- Air cooling is sufficient and preferred

- Thermal load aligns well with building characteristics

- Mini-split upgrade is the only major environmental change required

- Modular expansion avoids early over-spend

- Design avoids repeating EX4100-style platform risk

14. Next Logical Steps

- Finalize rack size (U height)

- Confirm electrical (120V vs 240V availability)

- Select mini-split model (18k BTU)

- Lock chassis model for compute node

- Build detailed BOM (Newegg + refurb)

- Plan phased GPU acquisition

End of Reference Document