# MECSAI HARDWARE FAULT CONTROL AND SCADA INTEGRATION REPORT

## Purpose

Define a hardened, insurable, and scalable approach for:

- Hardware-enforced DC fault protection

- Deterministic fault isolation

- SCADA-level observability and reporting

- MECSAI integration for analytics, trend detection, and operational governance

This document explicitly separates fault interruption from fault awareness. MECSAI never clears faults. It only sees them.

## 1. SYSTEM PHILOSOPHY (NON-NEGOTIABLE)

### Core Principle

Faults are cleared in hardware.

Faults are reported in software.

No PLC, SCADA, network, or AI system may be required to:

- Detect

- Decide

- Interrupt

If MECSAI is offline, powered down, or compromised:

- The system must still protect itself

- Fire risk must not increase

- Cascading failures must not occur

## 2. HARDWARE FAULT CONTROL ARCHITECTURE

### 2.1 Protection Tiering

#### Tier 0 - Device / String Level

- Solid-State Circuit Breakers (SSCBs) or E-Fuses

- Installed at:

  - SOEC stacks

  - Battery strings

  - DC-fed data hall segments

- Characteristics:

  - Autonomous detection

  - di/dt-based sensing

  - Clearing time <=10 microseconds

  - Fail-open behavior

#### Tier 1 - Zone Level

- SSCBs feeding:

  - SOEC blocks

  - Battery blocks

  - Data hall rows

- Characteristics:

  - Coordinated delay behind Tier 0

  - Prevents upstream collapse

  - Allows live isolation of submodules

#### Tier 2 - Backbone / Campus Isolation

- Mechanical or hybrid DC breakers

- Characteristics:

  - Fire department isolation

  - Maintenance lockout

  - Black-start segmentation

  - Not relied upon for fast protection

### 2.2 Mandatory Hardware Requirements

All SSCBs must:

- Operate without software

- Operate without communication

- Clear pole-to-pole and pole-to-ground faults

- Provide galvanic isolation post-trip

- Provide dry-contact or digital status outputs

Disallowed:

- Software-controlled breakers

- Network-dependent protection logic

- Centralized fault decision-making

## 3. SCADA INTEGRATION MODEL

### 3.1 SCADA Role Definition

SCADA is a read-only observer for fault events.

Allowed SCADA actions:

- Read breaker status

- Timestamp trip events

- Record fault magnitude

- Correlate multi-device faults

Disallowed SCADA actions:

- Clear faults

- Reset breakers automatically

- Override hardware lockouts

Manual reset only, after inspection.

### 3.2 Required SCADA Data Points per SSCB

Each SSCB must expose:

- Trip state (open/closed)

- Trip cause code

  - Overcurrent

  - Short-circuit

  - Ground fault

  - Thermal

  - Internal fault

- Peak fault current

- Fault duration

- Device temperature (pre and post trip)

- Trip count (lifetime and rolling window)

## 4. MECSAI INTEGRATION ARCHITECTURE

### 4.1 MECSAI Role

MECSAI is not a protection system.

MECSAI is a system intelligence layer.

MECSAI responsibilities:

- Aggregate SCADA fault data

- Detect patterns across subsystems

- Identify degrading components

- Recommend maintenance actions

- Optimize operating envelopes

MECSAI must never:

- Issue breaker commands

- Bypass lockouts

- Auto-reset protection devices

### 4.2 Fault Event Pipeline

- Hardware fault occurs

- SSCB clears fault locally

- SSCB latches open

- Status propagates to SCADA

- SCADA logs event

- MECSAI ingests event stream

- MECSAI analyzes trends

- MECSAI generates reports and alerts

This pipeline is one-directional.

## 5. FAULT CLASSIFICATION IN MECSAI

MECSAI should classify faults into:

### Category A - Benign / Transient

- Single event

- No recurrence

- No correlated faults

### Category B - Degrading Component

- Repeated trips on same device

- Increasing peak current

- Rising thermal baseline

### Category C - Systemic Risk

- Multiple devices tripping

- Cross-zone correlation

- Time-synchronized faults

Only Category C escalates to:

- Operations leadership

- Engineering review

- Potential controlled derating

## 6. REPORTING AND GOVERNANCE OUTPUTS

MECSAI must generate:

### Daily

- Fault summary by subsystem

- Trip counts

- Devices nearing threshold limits

### Monthly

- I2t trend analysis

- Thermal drift analysis

- Nuisance fault identification

### Annual

- Protection system performance report

- Insurability documentation

- Mean time between fault events

- Recommended protection upgrades

## 7. PROCUREMENT AND VENDOR LANGUAGE (KEY)

Include these requirements in all RFPs:

- Solid-state fault interruption <=10 microseconds

- Hardware-only detection and clearing

- Published I2t and let-through energy curves

- SCADA-readable fault telemetry

- Independent fail-open behavior

- FAT documentation for:

  - Pole-to-pole faults

  - Pole-to-ground faults

  - Worst-case inductance conditions

No vendor exceptions.

## 8. WHY THIS MATTERS

This architecture:

- Prevents cascading DC failures

- Reduces arc-flash risk by orders of magnitude

- Enables hot maintenance

- Improves SOEC uptime

- Satisfies insurer risk models

- Scales cleanly to Phase 3 and OSY deployments

## Final Statement

This design draws a hard line between:

- Physics (hardware protection)

- Awareness (SCADA)

- Intelligence (MECSAI)

That separation is what keeps the system safe, financeable, and expandable over a 100-year horizon.

If you want, next step:

- Convert this into a formal MECSAI ICD with signal definitions and fault taxonomies, ready for vendor alignment and Phase 19 hardening.