DC-BLDG-COOL-ENV-001

Cooling Envelope Specification – Rev A
Applies to: Data Center Buildings 1–16
Building 1 = Instrumented Proof-of-Concept

1. PURPOSE AND SCOPE

1.1 This document defines the mandatory cooling and thermal operating envelope for all AI data center buildings.

1.2 The envelope establishes:

- allowable coolant temperature bands

- rack-level and pod-level thermal limits

- CDU sizing and placement rules

- thermal ramp constraints

- fault isolation and leak containment doctrine

1.3 This envelope is binding for:

- mechanical design

- CDU procurement

- rack qualification

- tenant equipment acceptance

- MECSAI monitoring and analytics

Deviations require written owner approval.

2. COOLING ARCHITECTURE SUMMARY (FIXED)

2.1 Cooling method:

- Direct-to-chip liquid cooling is assumed

- Air cooling is auxiliary only (NICs, memory, PSU residuals)

2.2 Refrigerant:

- Ammonia prohibited inside building

- Building receives secondary loop fluid only via wall penetrations

2.3 Heat recovery:

- Heat Recovery Water Loop (HRWL) interfaces permitted

- Cooling reliability always takes priority over heat recovery

3. COOLANT TEMPERATURE ENVELOPE

3.1 Supply Temperature (to rack cold plates)

| Condition | Temperature |
| --- | --- |
| Nominal supply | 30°C (86°F) |
| Preferred operating band | 28–32°C |
| Max allowable sustained | 35°C (95°F) |
| Absolute ceiling (fault transient) | 38°C (100°F) |

3.2 Return temperature:

- No fixed cap, but delta-T must remain within CDU limits

3.3 Coolant type:

- Water or water/glycol mixture as required for freeze protection

- Dielectric fluids permitted only with explicit approval

4. RACK-LEVEL THERMAL ENVELOPE

4.1 Design Basis

| Parameter | Value |
| --- | --- |
| Nominal rack thermal load | 120 kW |
| Max sustained | 150 kW |
| Short-duration burst (≤5 min) | 165 kW |

4.2 Rack inlet air temperature (residual air cooling):

- Target: 20–30°C

- Max allowable: 35°C

4.3 Rack acceptance:

- Vendors must demonstrate cold-plate performance at 35°C supply

- No rack shall require chilled (<20°C) coolant

5. POD-LEVEL COOLING ENVELOPE (32-RACK POD)

5.1 Pod Thermal Capacity

| Parameter | Value |
| --- | --- |
| Nominal pod heat load | 3.84 MW |
| Max sustained | 4.80 MW |
| Absolute pod thermal cap | 5.28 MW |

5.2 Pod thermal capacity is enforced by:

- CDU sizing

- flow limits

- hardware isolation

6. CDU SIZING AND PLACEMENT RULES (LOCKED)

6.1 CDU placement:

- CDUs located only in utility bay

- No CDUs permitted in compute bay

6.2 Redundancy:

- N+1 CDU pair per pod group

- One CDU may fail without pod shutdown

6.3 CDU sizing:

- Each CDU pair must support:

  - 125% of nominal pod load

  - 100% of max sustained pod load

6.4 Flow control:

- Variable-speed pumping required

- Flow limits enforced per pod

7. THERMAL RAMP RATE LIMITS (CRITICAL)

7.1 Rack-Level Thermal Ramp

| Condition | Limit |
| --- | --- |
| Normal ramp | ≤1.5°C/min |
| Fast ramp | ≤3.0°C/min |

7.2 Pod-Level Thermal Ramp

| Condition | Limit |
| --- | --- |
| Normal | ≤1.0°C/min |
| Emergency shedding | Immediate |

7.3 Ramp enforcement:

- Achieved via:

  - flow control

  - CDU response

  - workload ramp coordination

- MECSAI observes but does not directly throttle pumps or valves

8. LEAK CONTAINMENT AND FAULT ISOLATION

8.1 Leak doctrine:

- All expected leak points reside in utility bay

- Compute bay must remain dry at all times

8.2 Mandatory containment:

- CDU underpans with leak sensors

- Gravity drain to utility bay trench

- Isolation valves at:

  - CDU inlet/outlet

  - Pod interface panel

8.3 Leak response:

- Hardware isolation first

- Alarm propagation second

- Manual intervention required to reset

9. ZONE-LEVEL THERMAL ISOLATION

9.1 Each 150-ft zone is a thermal fault domain.

9.2 Zone isolation:

- Cooling loops segmented by zone

- Failure in one zone must not propagate

9.3 HRWL interaction:

- Heat recovery disabled automatically if:

  - supply temp exceeds band

  - CDU capacity margin <20%

10. BUILDING-LEVEL THERMAL ENVELOPE

| Parameter | Value |
| --- | --- |
| Nominal building heat rejection | 123 MW |
| Max sustained | 154 MW |
| Absolute ceiling | 168 MW |

This aligns with the electrical envelope intentionally.

11. INSTRUMENTATION (BUILDING 1 – POC)

Building 1 shall include enhanced thermal instrumentation:

- Supply/return temp per CDU

- Flow rate per pod

- Delta-T tracking

- Leak detection timestamps

- Correlation to electrical ramp events

Telemetry feeds MECSAI for:

- degradation trending

- hotspot detection

- predictive maintenance

MECSAI shall not actuate valves or pumps directly.

12. TENANT ACCEPTANCE REQUIREMENTS

12.1 Tenant equipment must:

- operate with ≥30°C coolant

- tolerate ≥35°C supply excursions

- provide documented thermal ramp behavior

12.2 Equipment requiring chilled water or sub-ambient cooling is prohibited.

13. PROHIBITIONS

- No chilled water dependency

- No coolant below 20°C

- No CDUs in compute bay

- No cross-zone coolant interconnection

- No software-only leak response

14. REVISION CONTROL

- Rev A applies to Building 1 as Proof-of-Concept

- Buildings 2–16 inherit Rev A unless revised

- Revisions require operational data justification