DC-BLDG-ELEC-ENV-001

Electrical Envelope Specification – Rev A
Applies to: Data Center Buildings 1–16
Building 1: Instrumented Proof-of-Concept

1. PURPOSE AND SCOPE

1.1 This document defines the mandatory electrical operating envelope for all AI data center buildings at the Heber Campus.

1.2 The envelope establishes:

- allowable rack power density

- pod-level and zone-level power limits

- ramp rate constraints

- fault isolation requirements

- monitoring and telemetry boundaries

1.3 This envelope is binding for:

- architectural layout

- electrical engineering

- equipment procurement

- tenant contracts

- MECSAI integration

Deviations require written owner approval.

2. POWER ARCHITECTURE SUMMARY (FIXED)

2.1 Power source:

- Campus-owned generation (nuclear, solar, biomass)

- Building fed via campus DC backbone

2.2 Building intake:

- Heavy DC feed via wall penetrations only

- No roof penetrations permitted

2.3 Internal distribution:

- Overhead DC busway

- Pod-group tap boxes

- Hardware-cleared fault domains

3. RACK-LEVEL POWER ENVELOPE

3.1 Design Basis (Rev A)

| Parameter | Value |
| --- | --- |
| Nominal rack power | 120 kW per rack |
| Allowable sustained max | 150 kW per rack |
| Short-duration burst (≤5 min) | 165 kW |
| Minimum supported density | 80 kW per rack |

3.2 All racks, regardless of tenant, must be capable of operating safely anywhere within this envelope.

3.3 No rack shall exceed 150 kW sustained without explicit written approval.

4. POD-LEVEL POWER ENVELOPE (32-RACK POD)

4.1 Nominal Pod Capacity

| Parameter | Value |
| --- | --- |
| Pod size | 32 racks |
| Nominal pod load | 3.84 MW (32 × 120 kW) |
| Max sustained pod load | 4.80 MW |
| Absolute pod cap | 5.28 MW (short burst only) |

4.2 Pod capacity is defined by distribution limits, not by compute demand.

4.3 Each pod is a hard electrical fault domain.

5. ZONE-LEVEL POWER ENVELOPE (150-FT ZONE)

Each zone contains 8 pods.

5.1 Zone Capacity

| Parameter | Value |
| --- | --- |
| Nominal zone load | 30.7 MW |
| Max sustained zone load | 38.4 MW |
| Absolute zone cap | 42 MW |

5.2 Zones are electrically isolated such that:

- a zone fault does not propagate to adjacent zones

- load shedding or ramp control may be applied per zone

6. BUILDING-LEVEL POWER ENVELOPE

6.1 Building Capacity (Rev A)

| Parameter | Value |
| --- | --- |
| Nominal building load | 123 MW |
| Max sustained building load | 154 MW |
| Absolute building cap | 168 MW |

This is intentional overbuild. The building is not power-constrained.

6.2 Buildings 2–16 inherit this envelope unless revised by Rev B.

7. RAMP RATE AND TRANSIENT CONTROL (CRITICAL)

7.1 Rack-Level Ramp Limits

| Condition | Limit |
| --- | --- |
| Normal ramp | ≤ 10 kW/sec per rack |
| Fast ramp (approved workloads) | ≤ 25 kW/sec per rack |

7.2 Pod-Level Ramp Limits

| Condition | Limit |
| --- | --- |
| Normal ramp | ≤ 200 kW/sec per pod |
| Fast ramp | ≤ 500 kW/sec per pod |

7.3 Zone-Level Ramp Limits

| Condition | Limit |
| --- | --- |
| Normal ramp | ≤ 1 MW/sec per zone |
| Emergency shedding | Immediate (hardware enforced) |

7.4 Ramp limits are enforced by distribution design and contractual workload classification, not software throttling alone.

8. FAULT ISOLATION AND PROTECTION (NON-NEGOTIABLE)

8.1 Fault clearing:

- All electrical faults must be cleared in hardware

- No PLC, SCADA, or AI system may be required to clear faults

8.2 Fault domains:

- Rack → Pod → Zone → Building

- Fault propagation must stop at the smallest possible domain

8.3 Protection devices:

- Solid-state or hybrid DC breakers permitted

- Mechanical breakers permitted at zone/building boundaries only

- Automatic reset prohibited

8.4 MECSAI:

- May observe and analyze faults

- May not reset breakers

- May not override protection logic

9. POWER QUALITY REQUIREMENTS

9.1 Voltage tolerance:

- ±5% steady-state

- ±10% transient (≤200 ms)

9.2 Harmonics:

- Must meet vendor and insurance limits at pod interface

- Harmonic mitigation required if tenant equipment exceeds limits

9.3 Grounding:

- Dedicated DC grounding bus per pod

- Zone bonding network tied to building ground ring

10. INSTRUMENTATION AND TELEMETRY (BUILDING 1 POC)

Building 1 shall include expanded electrical instrumentation, including:

- Rack-level power monitoring (sampled)

- Pod-level power meters (mandatory)

- Zone-level meters (mandatory)

- Voltage, current, and transient logging

- Breaker trip cause codes

- Thermal correlation points

All telemetry feeds MECSAI for analytics only.

11. TENANT AND WORKLOAD REQUIREMENTS

11.1 Tenant equipment must:

- declare max rack power

- declare ramp behavior

- comply with pod-level envelope

11.2 Workloads must be classified:

- Tier 0 – must-run

- Tier 1 – priority

- Tier 2 – deferrable / throttle-able

11.3 Non-compliant equipment may be denied connection.

12. PROHIBITIONS

- No software-only fault protection

- No uncontrolled ramping

- No rack exceeding envelope

- No cross-zone power backfeeding

- No tenant-installed protection devices without approval

13. REVISION CONTROL

- Rev A applies to Building 1 as Proof of Concept

- Buildings 2–16 inherit Rev A unless revised

- Revisions require documented operational evidence