Proceeding with Rev A baseline. This is now the locked interior architecture spec for Buildings 1-16 using the 160 ft x 600 ft template, 32-rack pods, 4-block compute bay, 60 ft lowered utility bay, 4 zones, scooters + robots, and distributed CDU groups.

This is not CAD. It is the contract-grade architecture definition the CAD team will draw from.

## DC-BLDG-INT-001

## Data Center Interior Architecture - Rev A Baseline

## Building Template for Buildings 1-16

- BUILDING ENVELOPE AND STRUCTURAL CONSTANTS (LOCKED)

- Overall footprint: 160 ft (W) x 600 ft (L) = 96,000 sqft

- Interior clear height: 30 ft (clear to bottom chord / lowest obstruction)

- Structural column line: single line at the 60/100 bay interface only

- Roof: dual slope; no roof penetrations (all wall penetrations only)

- Exterior buffers: 2 ft clear buffer along both exterior long walls inside compute bay

- Truss spacing: 10 ft on center

- Roof framing: designed for site-specific ASCE 7 snow load plus drift at parapets

- Collateral load allowance: structure must support overhead busway, cable trays, ducting, and piping racks (to be finalized by engineer, but explicitly included)

- BAY CROSS SECTION (LOCKED)

2.1 Compute Bay

- Width: 100 ft clear span

- Purpose: racks only, aisles only, no CDU maintenance work, no wet work

2.2 Utility Bay

- Width: 60 ft

- Floor elevation: 1 ft lower than compute bay floor

- Floor slope: 1-2% toward center trench drain

- Center trench drain: continuous full length with grates rated for carts and scooters

- Purpose: wet work containment, CDUs, manifolds, valve stations, power and network distribution, parts storage, workstations, mobility lanes, robot docking

- COMPUTE BAY RACK GEOMETRY (LOCKED)

3.1 Rack Row Blocks Across Width

Compute bay contains 4 double-row blocks across:

Double-row block width (each):

- Cold aisle: 5 ft

- Rack depth zone: 5 ft

- Hot aisle: 4 ft

- Rack depth zone: 5 ft

- Cold aisle: 5 ft

Total block width: 24 ft

Compute bay width allocation:

- 4 blocks x 24 ft = 96 ft

- Remaining 4 ft = 2 ft buffer at each exterior wall line (interior side)

3.2 Row Count

- Each double-row block = 2 rack rows

- Total rack rows across width: 4 blocks x 2 rows/block = 8 rack rows

3.3 Cross Aisles

- Zone boundary cross aisle: 10 ft (minimum)

- Mid-zone cross aisle: 10 ft (implemented in each zone)

- Row-end clearance: 6 ft minimum at all row ends

- LENGTH SEGMENTATION AND ZONING (LOCKED)

Building length 600 ft is segmented into 4 operational zones:

- Zone A: 0-150 ft

- Zone B: 150-300 ft

- Zone C: 300-450 ft

- Zone D: 450-600 ft

Cross aisles:

- Primary cross aisle at each zone boundary (150, 300, 450): 10 ft

- Mid-zone cross aisle inside each zone (75, 225, 375, 525): 10 ft

Purpose of zoning:

- Limits walking distance and incident scope

- Defines fault domains (power/cooling isolation per zone)

- Enables distributed service nodes and robot docking

- POD STANDARD AND POD PACKING (LOCKED)

5.1 Pod Definition

- Pod size: 32 racks

- Pod is the atomic unit for:

  - cooling distribution (CDU group)

  - power distribution (busway taps and protective domain)

  - leak detection zone

  - operational ownership and work orders

  - tenant allocation boundaries (if needed)

5.2 Pod Packing Baseline

Baseline is 8 pods per zone:

- Pods per zone: 8 pods

- Racks per zone: 8 pods x 32 racks = 256 racks

- Total racks per building: 4 zones x 256 racks = 1,024 racks (Rev A baseline)

Interpretation:

- Each zone is planned as 8 pod groups served from the utility bay.

- Each pod group maps cleanly to an isolation and maintenance domain.

- COOLING ARCHITECTURE INSIDE THE BUILDING (REV A)

6.1 Philosophy

- Direct-to-chip liquid cooling assumed for AI racks.

- Ammonia does not enter building. Building receives secondary loop(s) via wall penetrations to HX yard.

- Utility bay is the wet work and cooling distribution zone.

6.2 CDU Strategy (LOCKED AS “DISTRIBUTED PER POD GROUP”)

- CDUs are distributed per pod group, not centralized at a single node.

- Baseline: 1 CDU pair (N+1) per pod group.

- CDU pairs are located in the utility bay aligned with their respective pod groups.

- Each CDU pair has:

  - isolation valves (supply/return)

  - bypass line

  - strainers/filters

  - leak detection underpan

  - local drain path to trench drain

  - instrumentation: flow, supply/return temp, delta-P, conductivity (as needed), alarms

6.3 Liquid Interfaces

- Each pod group receives:

  - supply and return headers from utility bay

  - quick disconnect manifolds at controlled interface panels

  - leak detection at interface panels

6.4 Leak Containment Doctrine

- Any expected leak-prone work happens in utility bay only.

- Utility bay floor slope and trench drain are the primary containment mechanism.

- Compute bay remains dry policy: no hose-down, no wet maintenance.

- POWER ARCHITECTURE INSIDE THE BUILDING (REV A)

7.1 Philosophy

- Building receives heavy DC feed from campus backbone.

- Building distributes power with modular segmentation by zone and pod group.

- Hardware protection clears faults locally; software observes.

7.2 Distribution Inside Building

- Main busway trunks run the length of the building (overhead).

- Tap boxes drop from busway to pod groups through controlled interface panels.

- Protective zones align with:

  - pod group

  - zone A/B/C/D boundaries

- Utility bay contains:

  - DC switchgear zones (where required)

  - protective devices

  - grounding and test points

  - serviceable access to taps and disconnects

7.3 Operational Control

- MECSAI sees power telemetry and fault state.

- MECSAI never clears faults and never commands protective devices.

- NETWORK AND LOW VOLTAGE ARCHITECTURE (REV A)

- Fiber enters into MMR located at one end of building (exact placement is site-driven).

- Primary fiber trunk runs in utility bay overhead lanes.

- Pod group drops route from utility bay to compute bay at defined interface panels.

- Cable make-up and testing benches live in service nodes in utility bay.

- UTILITY BAY INTERNAL LAYOUT (LOCKED)

9.1 Mobility Lanes

- Scooter lane: 6 ft clear, full length

- Robot lane: 4 ft clear, full length

- Both lanes are in the utility bay, not in the compute bay.

- Scooter and robot traffic never enters compute aisles.

9.2 Trench Drain

- Centered in utility bay full length

- Grated cover rated for carts and scooters

- Cleanouts at each service node (150 ft intervals)

- Designed for rapid drainage of spills and cleanup events

9.3 Service Nodes (LOCKED AT 150 FT INTERVALS)

Service node at each zone boundary location:

- At approximately: 150, 300, 450 (and optionally at 0 and 600 as end nodes)

Rev A baseline includes service nodes at each zone boundary plus end-cap support areas.

Each service node includes:

- Parts storage cages (high-turn spares)

- Workstations for cable make-up and component testing

- Scooter docking and charging

- Robot docking and charging

- Spill kit station

- Wet maintenance bench zone with containment

- Labeling and QR inventory integration points

- SAFETY AND EGRESS (REV A HIGH LEVEL)

- No scooter operation in compute bay.

- Pedestrian-only transitions between utility bay and compute bay at designated points.

- Emergency egress doors at both ends of building plus code-driven spacing along length (final by architect).

- Fire and smoke zoning aligns with the 4 zones, with boundaries at 150 ft segments.

- Lighting and aisle marking designed for rapid wayfinding across zones.

- OPERATIONS MODEL (REV A)

- Techs travel primarily in utility bay using scooters for rapid response.

- Robots perform repetitive logistics tasks along the utility bay.

- Compute bay stays uncluttered and service work is staged from the utility bay.

- Each 150 ft zone functions as a semi-independent operational cell:

  - local spares

  - local tools

  - local CDU groups

  - local isolation boundaries

- REPEATABILITY RULE FOR BUILDINGS 1-16 (LOCKED)

- All Buildings 1-16 share:

  - the same 160 x 600 geometry

  - the same 4-zone segmentation

  - the same 4-block compute bay

  - the same 60 ft lowered utility bay with trench drain

  - the same pod group and CDU distribution logic

  - the same mobility doctrine (scooters + robots in utility bay only)

- Tenant mix changes do not change geometry. Only pod allocation changes.

- OPEN ITEMS TO BE ENGINEERED NEXT (NOT BLOCKERS, BUT NEXT WORK PACKAGE)

- Exact rack pitch per row (allowing for manifold clearance and vendor rack depths)

- Exact CDU sizing per pod group (based on rack kW targets and coolant temps)

- Exact power voltage window and protective device selection by pod group

- Detailed egress door spacing and fire-rating strategy by zone

- Final structural collateral load schedule for overhead infrastructure

- Final drainage sizing and maintenance access details for trench drain system

## NEXT DELIVERABLES (IMMEDIATE)

If you want, next I will produce these as Rev A drawings/specs in the same style:

- Dimensioned interior plan callouts (compute bay blocks, cross aisles, zones, pod group placement)

- Utility bay lane and service node layout sheet

- Pod Group Interface Panel standard (power + liquid + fiber penetrations)

- CDU group placement rule sheet and leak containment doctrine detail

Say which one you want first and I will generate it.