HDS-DC-EVERGREEN-001

Evergreen Compute Refresh and Rack Slot Doctrine - Rev A
Document Class: Engineering + Operations Doctrine
Status: Draft - Internal
Owner: Atlas Systems Group - Hermes Data Systems
Applies To: All terrestrial HDS data center buildings and all future orbital DC translations

1. Purpose

This doctrine ensures Hermes data centers remain technologically current over a 20+ year building life while avoiding redesign cycles driven by silicon changes.

The building and campus infrastructure are long-life assets. The rack payload is a short-life asset.

This doctrine defines:

- rack slot envelopes that are vendor-agnostic

- modular retrofit rules

- refresh cadence and sequencing

- lane partitioning for accelerator ecosystems

- contractual and operational boundaries for mixed-generation deployments

2. Core Principle

Hermes does not build data centers around chips.

Hermes builds data centers around:

- power and thermal envelopes

- standardized interfaces

- modular isolation domains

- controlled refresh and replacement cadence

Chips and rack designs must conform to Hermes envelopes, not the reverse.

3. Asset Life Segmentation

3.1 Layer A - 20+ Year Assets (Non-Replaceable)

- building envelope and roof doctrine

- structural bays and clear spans

- wet/dry bay separation (utility vs compute)

- trench drain and containment geometry

- MMR and duct bank routing

- utility corridors and egress

3.2 Layer B - 10-15 Year Plant Equipment (Replace-in-Place)

- busway trunks and tap systems

- CDU groups and pump skids (modular replacement)

- secondary loop piping manifolds and isolation valves

- switchgear bays and protection zones (modular panels)

- fiber trunks and distribution frames

3.3 Layer C - 3-5 Year Compute Payload (Always Refreshed)

- racks and servers

- accelerators (GPU/ASIC)

- ToR and fabric gear

- storage tiers

- rack-level power shelves and manifolds

Layer C is designed for continuous rolling refresh.

4. Rack Slot Standard (Vendor-Agnostic)

Racks shall be deployed only if they conform to one of the defined rack slot envelopes.

4.1 Slot Classes

Slot S - Standard

- sustained rack power: 80-120 kW

- peak burst (<=5 min): 140 kW

Slot H - High Density

- sustained rack power: 120-180 kW

- peak burst (<=5 min): 210 kW

Slot X - Experimental / Future

- sustained rack power: 180-250 kW

- peak burst (<=5 min): 300 kW

- deployment limited to designated experimental pods only

Hermes is not required to support Slot X across all buildings. Slot X is optional capacity reserved for future silicon.

5. Thermal Envelope Requirements Per Slot

All rack types must operate within Hermes coolant envelope bands.

5.1 Coolant Supply Temperature

- nominal: 30C

- preferred band: 28-32C

- max sustained: 35C

- absolute transient ceiling: 38C

No rack may require chilled coolant (<20C).

5.2 Flow and Delta-P

- racks must declare required flow rate at each power band

- racks must declare delta-P across rack manifold at nominal flow

- racks exceeding Hermes delta-P envelope require local engineering approval

6. Interface Panel Standardization

Every pod group uses standardized interface panels for:

- power drops

- liquid supply/return

- fiber drops

- leak detection and telemetry points

Interface standards must be defined as:

- mechanical connector standards

- quick disconnect standards

- electrical connector / busway tap standards

- minimum telemetry set

The purpose is to allow rack refresh without reengineering building infrastructure.

7. Accelerator Ecosystem Lanes (Silicon Neutrality)

Hermes supports multiple accelerator ecosystems through “lanes.”

Example lanes:

- Lane N: NVIDIA ecosystem (Rubin/B-series class)

- Lane A: AWS Trainium/Inferentia ecosystem

- Lane C: customer-proprietary or future custom silicon

7.1 Lane Rules

- a pod is assigned one lane

- mixed-lane pods are prohibited

- zones may contain multiple lanes but boundaries must be explicit

- lane choice may not alter building interface standards

Lane neutrality is critical for long-term market optionality.

8. Evergreen Refresh Doctrine

8.1 Standard Refresh Cadence

- target: 25% of racks refreshed per year

- full fleet refreshed every 4 years typical

- partial refresh cycles allowed by customer contract

8.2 Refresh Unit of Work

Refresh occurs at the pod group level:

- pod group is isolated

- racks removed

- infrastructure verified

- new racks installed

- acceptance testing executed

- pod returned to service

8.3 Refresh Scheduling

MECSAI schedules refresh windows using:

- customer workload tier

- utilization and congestion

- power and cooling margins

- contractual downtime allowances

No refresh action may violate Tier 0 uptime obligations.

9. Mixed Generation Coexistence

Hermes allows mixed generations of racks and accelerators, but only within governance:

- older racks must remain within slot envelopes

- mixed generations may coexist in a zone if lane boundaries are preserved

- network fabrics must be engineered for interoperability or segmented

Mixed generation deployments are treated as normal, not an exception.

10. Acceptance and Commissioning for Refresh

Any refresh must pass a defined acceptance sequence:

- interface verification (power, liquid, fiber)

- leak test and pressure hold

- thermal ramp validation

- power ramp validation

- telemetry verification

- workload test run

Failure halts acceptance and returns pod to safe state.

11. Spare Strategy and Lifecycle Management

Hermes maintains a standard spare strategy:

- spare CDUs and pumps per building

- spare interface panel components

- spare busway tap assemblies

- spare rack quick disconnect assemblies

- standardized parts across buildings and campuses

Vendor-specific rack spares are managed separately by lane and customer contract.

12. Prohibitions

- racks requiring chilled coolant are prohibited

- mixed-lane pods are prohibited

- ad hoc rack modifications that change interface standards are prohibited

- any refresh that bypasses acceptance gates is prohibited

- any vendor lock-in that prevents lane neutrality is prohibited

13. Orbital Translation Note

This doctrine is designed specifically to translate into orbital data center environments.

By enforcing:

- slot envelopes

- modular replacement

- strict isolation and acceptance
Hermes ensures that orbital DCs can be refreshed and upgraded with minimal human intervention.

14. Revision Control

Rev A establishes the initial doctrine.
Revisions require:

- measured operational evidence

- impact analysis on infrastructure

- governance approval