HDS Pod Group Evergreen Refresh Playbook
Step-by-Step Runbook for Rack Refresh Operations

Document ID: HDS-DC-REFRESH-PLAYBOOK-001
Revision: Rev A
Status: Draft - Internal
Owner: Atlas Systems Group - Hermes Data Systems
Date: 2026-01-12

# 1. Purpose

Provide a repeatable runbook for refreshing racks and IT payload at the pod group level without disrupting adjacent pods, while maintaining safety boundaries and contractual uptime obligations.

# 2. Scope

Applies to all Hermes buildings. Unit of work is a 32-rack pod group within a 150-ft zone. All work is executed from the utility bay; compute bay remains dry and uncluttered.

# 3. Roles and Authority

- Operations Manager: authorizes refresh windows and approves gates.
- Facilities Lead: executes LOTO and verifies isolation.
- Network Lead: manages fabric changes and validates connectivity.
- MECSAI: schedules windows, recommends actions, logs events, produces reports. MECSAI does not clear faults or override interlocks.
- Safety PLC/SIS: authoritative for safety states.

# 4. Preconditions

- Maintenance window approved.
- Workload drain plan approved.
- Replacement racks staged at nearest service node.
- Rollback plan prepared (retain old racks until acceptance).
- Permits and safety reviews complete.

# 5. Refresh Gates (Must Pass in Order)

Gate R0 - Schedule Authorization
Gate R1 - Workload Drain
Gate R2 - Electrical Isolation and LOTO + Cooling Isolation
Gate R3 - Rack Removal and Interface Inspection
Gate R4 - Install New Racks and Connect Interfaces
Gate R5 - Commission (Leak test, pressure hold, power/thermal ramps, telemetry)
Gate R6 - Acceptance (validation workloads, sign-off, return to service)

# 6. Step-by-Step Runbook

6.1 Step 1 - Schedule and Notify (Gate R0)

- Confirm CMMS work order and approved window.
- MECSAI generates pre-refresh snapshot: utilization, thermal margin, recent faults.
- Notify operations, facilities, network, security, customer contact.

6.2 Step 2 - Workload Drain (Gate R1)

- Migrate workloads and checkpoint training jobs.
- Verify inference reroutes.
- Confirm pod group drained and in approved state.

6.3 Step 3 - Electrical Isolation and LOTO (Gate R2)

- Open pod group disconnects at utility bay tap box.
- Apply LOTO.
- Verify absence of voltage at rack feeds.
- Record status and trip counters.
- MECSAI logs isolation state.

6.4 Step 4 - Cooling Isolation (Gate R2)

- Close isolation valves at CDU group and interface panel.
- Depressurize per procedure into trench drain containment if required.
- Verify leak sensors normal and trench drain clear.

6.5 Step 5 - Rack Removal (Gate R3)

- Disconnect QDs using dry-break procedure.
- Cap and label connectors.
- Remove racks and stage in quarantine until acceptance complete.
- Inspect interface panel and overhead drops.

6.6 Step 6 - Install New Racks (Gate R4)

- Install racks per lane and slot assignment.
- Connect power, liquid, fiber.
- Verify labeling and mapping.

6.7 Step 7 - Leak Test and Pressure Hold (Gate R5)

- Pressurize and hold per engineering spec.
- Confirm no leaks and no alarms.
- If failed: isolate, drain, correct, repeat.

6.8 Step 8 - Power and Thermal Ramps (Gate R5)

- Energize pod group.
- Ramp: 10%, 25%, 50%, 75%, 100%.
- Confirm voltage stability.
- Confirm coolant envelope and flow.
- Any out-of-envelope event triggers hold and investigation.

6.9 Step 9 - Telemetry Verification (Gate R5)

- Verify required tags, time sync, and alarms.
- MECSAI generates post-commission report.

6.10 Step 10 - Acceptance and Return to Service (Gate R6)

- Run validation workloads.
- Confirm stability and performance.
- Customer sign-off if applicable.
- Release LOTO and return to service.

# 7. Rollback and Failure Handling

Rollback triggers:
- persistent leaks
- power instability beyond envelope
- thermal envelope violation
- fabric connectivity failure

Rollback procedure:
- isolate and de-energize pod group
- reinstall last known good racks if required
- restore pre-refresh configuration
- generate incident report and corrective action plan

# 8. MECSAI Hooks and Required Logs

- pre-refresh snapshot
- drain completion timestamp
- isolation timestamps
- pressure hold results
- ramp traces
- acceptance test outcomes
- return-to-service timestamp
- monthly refresh summary

# 9. Post-Refresh Closeout

- Update asset registry: rack model, lane assignment, slot class, firmware versions.
- Update spare inventory counts.
- Archive prior configuration and logs.
- Close work order with acceptance evidence attached.

# 10. Prohibitions

- No wet work in compute bay.
- No bypass of LOTO.
- No acceptance without documented tests.
- No MECSAI commands that actuate safety or protection devices.

# 11. Revision Control

Rev A establishes baseline refresh workflow. Site-specific variations must be documented and approved.