HDS-NET-001
Hermes Network Strategy Doctrine
Carrier Diversity, Private Backbone, ASN/Peering Roadmap

Owner: Atlas Systems Group - Hermes Data Systems
Revision: Rev A
Status: Draft - Internal
Date: 2026-01-12

# 1. Purpose

Define the Hermes Data Systems network strategy for multi-campus AI data centers. This doctrine establishes carrier diversity, meet-me room (MMR) standards, private backbone strategy, and the phased path to operating as an autonomous system (ASN) with peering, without becoming a retail ISP.

# 2. Core Principles

- Reliability: no single cut, POP failure, or carrier outage may isolate a campus.
- Diversity: physical path diversity matters more than the number of carriers.
- Neutrality: Hermes must remain silicon- and cloud-neutral; network policy must support this.
- Security: strict segmentation; tenant traffic never shares control-plane pathways.
- Federation-first: the inter-campus backbone is strategic infrastructure, not an afterthought.
- Phased maturity: start as a multi-homed customer; evolve into a private backbone operator; then obtain ASN and peer.

# 3. Connectivity Control Levels

Level 1 - ISP Customer (colo-style): buy transit from carriers; minimal control.
Level 2 - Hermes Network Operator (required): own internal routing/backbone; buy transit at edges.
Level 3 - Hermes ASN + Peering (planned): multi-home BGP, peer at IXPs, optionally offer private peering services.

Hermes does not pursue retail ISP operations. Hermes pursues enterprise backbone control and routing sovereignty.

# 4. Campus Network Architecture Standard

4.1 Dual Meet-Me Rooms (Mandatory)

- Each campus shall have two physically separated meet-me rooms: MMR-A and MMR-B.
- MMR-A and MMR-B must have:
  - separate duct-bank entrances and conduit paths
  - separate power and cooling feeds
  - separate security zones and access control
  - independent patch bays and ODF/MDF panels
- A single building event (fire, flood, mechanical) shall not disable both MMRs.

4.2 Diverse Fiber Entrances (Mandatory)

- Two diverse duct-bank routes from campus boundary to MMR-A and MMR-B.
- Routes shall be geographically separated where feasible (different road corridors/easements).
- Conduits shall be armored, mapped, and marked; burial depth per code and local risk.
- Acceptance requires proof of diverse pathing (as-builts plus carrier confirmation).

4.3 Per-Building Connectivity (Mandatory)

- Each building shall have dual diverse fiber paths back to MMR-A and MMR-B.
- Buildings shall have separate switch rooms or diverse riser paths so one conduit cut does not isolate a building.
- Spine-leaf fabrics are required internally; redundant leaf pairs per pod group.

# 5. Carrier Diversity Policy

Hermes does not pursue 'six ISP' redundancy for its own sake. Hermes pursues meaningful upstream and physical diversity.

5.1 Minimum Carrier Mix per Campus

- Minimum three (3) carriers at each campus edge:
  - Carrier 1: major long-haul provider
  - Carrier 2: regional fiber provider
  - Carrier 3: alternate backbone / POP diversity provider
- Carrier selection must avoid shared upstream POP dependencies.
- At least two carriers must terminate in each MMR (balanced distribution).

5.2 Transit vs Peering vs Private Interconnect

- Transit: purchased for general internet reachability.
- Peering: used to reduce cost and improve latency once Hermes has ASN and presence at IXPs.
- Private interconnect: direct links to hyperscalers/sovereigns where required (contracted).

# 6. Inter-Campus Backbone Strategy

6.1 Objectives

- Provide deterministic east-west capacity for federation workloads.
- Ensure two independent routes between campuses wherever feasible.
- Support encryption and sovereign partitioning.
- Avoid reliance on public internet for core replication and federation.

6.2 Preferred Transport Options (Priority Order)

Option 1 - Dark Fiber Lease: Hermes lights fiber with its own DWDM gear (preferred).
Option 2 - Wavelength Services: buy 100G/400G waves, scalable by parallel waves.
Option 3 - Internet VPN: management traffic only; not acceptable for core federation.

6.3 Topology

- Hermes shall build ring topologies, not star topologies, to avoid single-point dependence.
- Regional rings are preferred (Heber-Holbrook-Winslow/I-40 POP loop, etc.).
- Inter-region interconnects shall be redundant and geographically diverse where feasible.

# 7. Federation Traffic Doctrine

- Default cross-campus federation mode is async-first:
  - hyperparameter sweeps
  - simulation batches
  - CAD/FEA farms
  - model checkpoint shipping
- Synchronous tightly coupled training is assumed intra-campus or within metro regions only.
- Data gravity rule: keep datasets local; move models and checkpoints by default.

# 8. Security and Segmentation

Minimum required network domains:
1) Tenant/customer data plane
2) Federation backbone plane
3) MECSAI control and telemetry plane
4) Security systems plane
5) Out-of-band management plane

Rules:
- Tenant traffic must never share control-plane pathways.
- MECSAI plane must support air-gapped operation where required.
- All inter-campus traffic is encrypted and policy-controlled.

# 9. ASN and Peering Roadmap (Phased)

Phase A - Early Campus (Single Campus)

- Dual MMR build standard.
- Multi-homed transit with three carriers.
- Wavelength services for initial inter-site links (if needed).

Phase B - Multi Campus (2-3 Sites Live)

- Lease dark fiber on primary corridors where feasible.
- Deploy DWDM and build private backbone.
- Implement Hermes routing policy across sites.
- Establish regional rings.

Phase C - Full Federation (6 Sites Scaling)

- Obtain an ASN and run multi-homed BGP.
- Establish presence at relevant IXPs (Phoenix, Las Vegas, Salt Lake, Denver as needed).
- Peer with major carriers and selective partners.
- Implement DDoS mitigation and scrubbing strategy.
- Offer private peering as a service only when aligned to Hermes customer contracts (not retail ISP).

# 10. Acceptance Tests and Evidence

Minimum acceptance evidence per campus:
- As-built conduit and duct-bank drawings showing diverse physical paths.
- Carrier letters confirming diverse route and POP separation.
- Failover test demonstrating loss of a carrier and/or MMR does not isolate campus.
- Inter-campus link failover test (ring reroute) for federation traffic.
- Security audit confirming segmentation and access controls.

# 11. Operations

- 24/7 NOC required at federation scale.
- Standardized monitoring and alerting across all sites.
- Change control for routing policy and security configuration is mandatory.
- MECSAI may monitor network health and recommend actions; network control remains under deterministic network operations authority.

# 12. Prohibitions

- Hermes shall not operate as a consumer/retail ISP.
- Hermes shall not rely on a single MMR or single duct-bank entry.
- Hermes shall not rely on public internet VPN for core federation.
- Hermes shall not commingle tenant traffic with MECSAI control traffic.

# 13. Next Actions

- Publish campus-specific carrier shortlists and POP diversity mapping.
- Define Heber-Holbrook backbone corridor strategy (dark fiber vs waves) and ring topology.
- Draft the Hermes Network ICD: interfaces between MMRs, buildings, and the inter-campus backbone.
- Develop DDoS mitigation procurement plan for Phase C.
- Establish network governance and change control procedures aligned to Atlas doctrines.