HDS-NET-HEBER-ADD-001
Heber Campus Network Redundancy Addendum
SR-260 Fiber Leg, I-40 Fiber Leg, and Starlink Tertiary Path

Parent Doctrine: HDS-NET-001
Owner: Atlas Systems Group - Hermes Data Systems
Revision: Rev A
Status: Draft - Internal
Date: 2026-01-12

# 1. Purpose

This addendum applies HDS-NET-001 to the Heber Campus and defines a practical, implementable redundancy plan using two physically diverse terrestrial fiber corridors plus a third non-terrestrial communications path for survivability. It does not replace HDS-NET-001. It supplements it with site-specific execution guidance.

# 2. Summary of Heber Connectivity Legs

Heber Campus connectivity shall be built on three legs:
Leg A (Primary terrestrial): SR-260 corridor (Payson <-> Heber <-> Show Low) using Sparklight-operated fiber.
Leg B (Secondary terrestrial): I-40 corridor tie-in via Winslow (or nearest practical I-40 POP) using an independent long-haul/backbone provider.
Leg C (Tertiary non-terrestrial): Starlink enterprise connectivity as an out-of-band and emergency continuity path.

# 3. Design Intent and Constraints

- The objective is corridor diversity and POP diversity, not 'number of ISPs'.
- A single backhoe event, local fire, or carrier outage must not isolate the campus.
- Starlink is not a replacement for primary/secondary fiber legs for tenant traffic. It is a survivability path.
- All carrier claims of diversity must be evidenced by route letters and POP mapping.

# 4. Meet-Me Room Requirements for Heber

Heber shall implement dual meet-me rooms (MMR-A and MMR-B) as defined in HDS-NET-001. Heber-specific requirements:
- MMR-A shall be fed by a dedicated duct-bank route aligned to the SR-260 corridor.
- MMR-B shall be fed by a dedicated duct-bank route aligned to the northbound I-40 corridor.
- Each MMR must be capable of terminating both Leg A and Leg B carriers.
- MMR-A and MMR-B must be separated physically such that a single building event cannot disable both.
- Each building must have dual diverse paths to both MMRs.

# 5. Leg A - SR-260 Corridor (Sparklight)

Leg A uses Sparklight fiber that runs through Heber along the SR-260 corridor (Payson to Show Low). Execution requirements:
1) Obtain a carrier route letter from Sparklight showing the physical route and confirming where the upstream POP is located.
2) Validate POP diversity: confirm that upstream backhaul does not share the same intermediate corridors or POP as Leg B.
3) Terminate Sparklight in both MMR-A and MMR-B where feasible. If not feasible, terminate in one and cross-connect to the other internally.
4) Require a defined handoff type: lit transit and/or wavelengths, with SLA and escalation contacts.

# 6. Leg B - I-40 Corridor Tie-In (Winslow)

Leg B provides corridor diversity via a northbound tie-in to I-40 at Winslow (or nearest practical POP along I-40). Execution requirements:
1) Select an independent provider that is not operationally dependent on Sparklight and does not share the same POP for upstream routing.
2) Prefer dark fiber or wavelength services for backbone capacity where commercially available; transit is acceptable as an interim.
3) Build a dedicated northbound duct-bank route from the campus to the I-40 tie-in corridor.
4) Terminate the I-40 provider in both MMR-A and MMR-B where feasible; otherwise cross-connect internally.
5) Require route evidence: fiber route maps or route letters showing physical separation from Leg A beyond the campus boundary.

# 7. Leg C - Starlink Tertiary Path

Starlink enterprise service is approved as the tertiary connectivity leg. Intended uses:
- Out-of-band management network continuity
- Emergency communications when both terrestrial legs are impaired
- Limited critical services continuity where bandwidth is not the limiting factor

Constraints:
- Starlink is not a substitute for primary or secondary fiber for tenant data plane or high-throughput federation.
- The redundancy plan shall not depend on hosting a Starlink gateway. Starlink ground gateway deployment is not assumed.
- Starlink must be integrated through a dedicated OOB edge and must not share control planes with tenant traffic.

# 8. Federation Traffic Guidance for Heber

Inter-campus federation for Hermes is async-first by doctrine. For Heber:
- Use Leg A and Leg B as primary federation egress options.
- Starlink is not used for large checkpoint shipping or dataset movement.
- Heber to Holbrook should prioritize private backbone options (dark fiber or dedicated waves) if corridor access exists.
- If only transit is available initially, encrypt federation traffic and cap synchronous coupling to intra-campus only.

# 9. Acceptance Tests and Evidence (Heber)

Heber acceptance requires documented evidence and tests:
9.1 Evidence Package
- As-built duct-bank and conduit drawings for both MMR-A and MMR-B ingress routes.
- Carrier route letters for Sparklight and the I-40 provider, including POP locations.
- POP diversity mapping showing independent upstream routing.
- Photos and labels of entrance vaults, conduits, and MMR termination panels.

9.2 Failover Tests
- Test 1: Disable Leg A and demonstrate campus remains reachable through Leg B.
- Test 2: Disable Leg B and demonstrate campus remains reachable through Leg A.
- Test 3: Disable MMR-A and demonstrate traffic fails over to MMR-B.
- Test 4: Disable MMR-B and demonstrate traffic fails over to MMR-A.
- Test 5: Disable both terrestrial legs and demonstrate Starlink maintains OOB management connectivity.

9.3 Reporting
- Record start/end timestamps, packet loss, route convergence time, and affected services.
- Archive BGP session logs (if applicable), edge router logs, and NOC confirmation.
- MECSAI may observe and report network health, but network operations remains the authority.

# 10. Implementation Sequence (Recommended)

Step 1: Build MMR-A and MMR-B with diverse campus ingress, power, and security.
Step 2: Contract Leg A (Sparklight) and obtain route evidence and POP mapping.
Step 3: Contract Leg B (I-40 provider) and obtain route evidence and POP mapping.
Step 4: Build northbound duct-bank route to I-40 corridor and terminate into both MMRs.
Step 5: Install Starlink enterprise as a dedicated OOB edge.
Step 6: Execute and record acceptance tests; publish Heber network acceptance report.

# 11. Prohibitions

- Do not accept carrier diversity claims without route letters and POP mapping.
- Do not rely on a single MMR.
- Do not use Starlink as primary tenant connectivity.
- Do not commingle tenant data plane with MECSAI control plane or OOB plane.

# 12. Revision Control

Rev A establishes the Heber-specific addendum. Subsequent revisions shall incorporate carrier selection details, site-specific conduit routes, and finalized POP locations once contracts are executed.